## Slide 1: Status of Fast Controller EPICS Supports for ITER Project
Vishnu Patel
ITER Organization
Control System Division
Disclaimer: The views and opinions expressed herein do not necessarily reflect those of the ITER Organization

## Slide 2: Content
Introduction
Hardware Architecture
Software Architecture
PXI-6259
Timing Board
PXIe-6368
PXI-6528
cRIO / FlexRIO bundles.
Conclusion

## Slide 3
Introduction of I&C Architecture

## Slide 4: Hardware Architecture

## Slide 5
Hardware Architecture

## Slide 6: Standard Hardware Support
Supported I/O boards:
  N.I. PXI-6682/PXI-6683H : Synchronization and timing (IEEE1588-2008 / TCN)
  N.I. PXI-6259: multi-function data acquisition
    16bits analog input channels (16 Diff. /32 Single Ended) (1.25MS/s)
    16bits analog output channels (4) (2.86 MS/s)
    digital input/output channels (48)
  N.I. PXIe-6368: High Performance multi-function data acquisition
    16bits analog input channels (16 Diff.) (Simultaneous, 2MS/s)
    16bits analog output channels (4) (3.3 MS/s)
    digital input/output channels (48)
  N.I. PXI-6528 : Digital I/O
    24 optically isolated input channels
    24 solid-state relay output channels
    ±60VDC channel to channel Isolation

## Slide 7: Standard Hardware Support
Supported cRIO I/O modules:
  N.I. 9425/9426 : Sinking / Sourcing Digital Input -7µS, 32 Channels 12/24V
  N.I. 9476 /9477: Sourcing - 500 µS / 6-36V /250mA
  : Sinking - 8 µS /5-60V /625 mA
    32 Channels Digital Output
  N.I. 9205 : 32 x AI (16-bit, ±200mV to ±10V, 250kS/s)
  N.I. 9264 : 16 x AO (16-bit, ±10V, isolation 60VDC, 25 kS/s/ch simultaneous )
Supported FlexRIO I/O board bundles:
  N.I. PXIe 7966R/5761R : FPGA / ADC Bundle (14-bits, 2.07Vpk-pk, 250MS/s, 4 ch + DIO)
  N.I. PXIe 7961R/6581 : FPGA / DIO Bundle (100MHz, 54 DIO)
  N.I. PXIe 7966R/1483 : FPGA / Image Acquisition Bundle
  Camera Link (10-tap, 80-bit images)
  20 to 85 MHz pixel clock, 4 TTL DO, 2 Optical DI, 1 Quadrature encoder input
    The Supported boards are listed in the ITER Catalog of I&C products - Fast Controllers (345X28).

## Slide 8: Software Architecture

## Slide 9
The main challenge for CODAC is INTEGRATION
CODAC Core System
Operation Applications
Software Applications

## Slide 10
PLC
PLC IOC
PSH IOC
PSH
CODAC Terminal
Operator Interface (OPI)
Alarm views
Data plots
Control System Studio HMIs
Alarm server
Archive Server
CODAC
CODAC Server
Alarm handling
Archiving
PSH:
I&C monitoring
PLCs Gateway
I&C coordination
Fast Controller:
I/O interface
HPN interfaces: TCN, SDN, DAN
RT control
PCF
IOC
I/O
Fast Controller
SDN
TCN
DAN
RT task
PON / CA
CODAC Core System (CCS)

## Slide 11: Fast Controller software
OS: Red Hat Enterprise Linux for the x86-64 architecture (RHEL x86_64)
  CCS 5.x -> RHEL 6.5
  CCS 6.x -> RHEL 7.0
For fast feedback control: real-time enabled RHEL MRG-R
  Optimized kernel for real-time applications
  More deterministic latencies / reduced jitter
Framework: EPICS and ASYN
  ITER adopted open source control system EPICS
  CCS 5.4 -> EPICS 3.15 , asynDriver 4.30
  CCS 6.0 -> EPICS 3.16 , asynDriver 4.31

## Slide 12: EPICS Device Support
  Basic EPICS Device Support
  PXI-6259: multi-function data acquisition.
asynDriver based Device Support
PXI-6682 & PXI-6683h : Synchronization and timing.
  PXIe-6368: High Performance multi-function data acquisition.
  PXI-6528 : Digital I/O.
  cRIO and flexRIO bundles.
Future device Support
  PXIe-6363: multi-function data acquisition boards.

## Slide 13: PXI 6259 DAQ Board

## Slide 14: PXI 6259 Main functions
All DAQ modes support
  Software timed acquisition
  Hardware timed acquisition
    Finite sample mode
    Continuous mode
AI/AO triggering support
  Start, Stop trigger
  Pause trigger (Activate/Deactivate DAQ/Data generation)

## Slide 15: PXI 6259 Board functions
General
  Device Information
  Device and Channel status
  Software version
Clock Settings
  Sampling rate
  Clock Source
  Clock divider
Triggering
  Set trigger (Software or Hardware)
  Pre & Post trigger
DIO configuration
Analog Output configuration.
General purpose counter
Signal routing

## Slide 16: Timing Boards (PXI-6682 & PXI-6683H)

## Slide 17: Timing Boards Functions
Receive ITER time as PTP (IEEE 1588-2008)
Synchronization of system time with Board time
Generate Future time events, Pulse and Clocks
  Front panel connector
  PXI backplane lines
Signal routing
Clock routing
Accurate Time-stamping of event
  Board triggers
  External events (Front panel connector & Backplane lines)
Pulse sequence Programming on the selected terminal.

## Slide 18: Timing Boards (PXI-6682 & PXI-6683H)
Synchronization(50ns rms)
Clock generation
Synchronized event generation.
Signal time stamping.
Common software for both boards
PFI0-PFI2 (FTEs and generated clocks)
Clock input (not in PXI-6683H)
Clock output
Clock board (10MHz)
Backplane clock (10MHz)
PXI trigger bus (8 lines)

## Slide 19: PXIe-6368 DAQ Board

## Slide 20: PXIe-6368 DAQ Board Function
Read Device information (Status, Software Version…)
Set configuration parameter for Analog Input
Dynamic AIO/DIO configuration with EPICS PVs.
Acquisition mode.
  Continuous
  Finite sample
  Retriggerable finite sample
  Reference triggered
waveform and ai record support for Analog input.
Board level and Channel level EPICS Template.

## Slide 21: PXI-6528 DIO Board

## Slide 22: PXI-6528 DIO Board Functions
Read Device information
Bit and Byte write/read on hardware port (3 input and 3 output ports)
Signal routine.
Watchdog configuration
Level change on watchdog
Level change detection
Input port filter
Output port Power up state
driver
interface
client / asynUser
Byte
bus controller (port)
Bit

## Slide 23: Compact RIO & Flex RIO

## Slide 24
Windows Host
Design Methodology

## Slide 25: cRIO & FlexRIO board functions
Read Device information (Status, Software Version…)
Dynamic IO configuration with EPICS PVs.
waveform and ai record support for Analog input.
DMA Acquisition and Data transfer between board and controller.
Image acquisition using cameralink – serial line for camera configuration.
Signal Generation (DDS)
Board level and Channel level EPICS Templates for each bundles.

## Slide 26
Conclusion
ITER Fast Controller EPICS device supports are stable.
It is well integrated with ITER CODAC Core System.
Developed templates are useful for fast application development.
We will continue to extend and improve the support.
Thank you